## RackPower
[8 empty] | OID | SYNTAX | MAX-ACCESS | UNITS | STATUS | DESCRIPTION
enterprises (.1.3.6.1.4.1) | rackPower (60967) | products (1) | alarms (1) | alarmNums |  |  |  | .1.3.6.1.4.1.60967.1.1.1 | Integer32 | read-only |  | current
|  |  |  | alarmTable | alarmEntry | alarmId | Alarm ID | .1.3.6.1.4.1.60967.1.1.2.1.1
[6 empty] | alarmDevID | Device ID | .1.3.6.1.4.1.60967.1.1.2.1.2
[6 empty] | alarmOid | Alarm OID | .1.3.6.1.4.1.60967.1.1.2.1.3
[6 empty] | alarmTime | Alarm time | .1.3.6.1.4.1.60967.1.1.2.1.4
|  |  |  | traps | trapAlarmEntryAdded |  | Alarm occurs | .1.3.6.1.4.1.60967.1.1.3.1 | NOTIFICATION-TYPE
[5 empty] | trapAlarmEntryRemoved |  | The alarm disappears | .1.3.6.1.4.1.60967.1.1.3.2 | NOTIFICATION-TYPE
|  |  | series （2） | SYS
|  |  |  | sys | identify | manufacturer | Equipment Manufacturer | .1.3.6.1.4.1.60967.1.2.1.1.1 | OCTET STRING | read-write |  | current
[6 empty] | softwareVersion | Software version | .1.3.6.1.4.1.60967.1.2.1.1.2 | OCTET STRING | read-only |  | current
[6 empty] | devIdentify | Device identification | .1.3.6.1.4.1.60967.1.2.1.1.3 | OCTET STRING | read-write |  | current
UPS
|  |  |  | ups | upsIndex | upsDevTotalNums | Number of devices | .1.3.6.1.4.1.60967.1.2.3.1.1 | Integer32 | read-only |  | current | The number of ups in the system
[6 empty] | upsCurrentDevID | Current device ID | .1.3.6.1.4.1.60967.1.2.3.1.2 | Integer32 | read-write |  | current | The current ups index of the follow data
[5 empty] | upsIdentify | upsManufacturer | Equipment Manufacturer | .1.3.6.1.4.1.60967.1.2.3.2.1 | OCTET STRING | read-write |  | current
[6 empty] | upsSoftwareVersion | Software version | .1.3.6.1.4.1.60967.1.2.3.2.2 | OCTET STRING | read-only |  | current
[6 empty] | upsDevIdentify | Device identification | .1.3.6.1.4.1.60967.1.2.3.2.3 | OCTET STRING | read-write |  | current
[5 empty] | upsStatus | upsPowerSource | Power supply | .1.3.6.1.4.1.60967.1.2.3.3.1 | INTEGER{none(0),ups(1),bypass(2)} | read-only |  | current
[6 empty] | upsBarrerySatus | Battery status | .1.3.6.1.4.1.60967.1.2.3.3.2 | INTEGER{disconnect(0),boost(1),float(2),discharge(3)} | read-only |  | current
[5 empty] | upsBypass | upsBypassVoltA | Bypass voltage A | .1.3.6.1.4.1.60967.1.2.3.4.1 | Integer32 | read-only | "0.1V" | current
[6 empty] | upsBypassVoltB | Bypass voltage B | .1.3.6.1.4.1.60967.1.2.3.4.2 | Integer32 | read-only | "0.1V" | current
[6 empty] | upsBypassVoltC | Bypass voltage C | .1.3.6.1.4.1.60967.1.2.3.4.3 | Integer32 | read-only | "0.1V" | current
[6 empty] | upsBypassCurrA | Bypass current A | .1.3.6.1.4.1.60967.1.2.3.4.4 | Integer32 | read-only | "0.1A" | current
[6 empty] | upsBypassCurrB | Bypass current B | .1.3.6.1.4.1.60967.1.2.3.4.5 | Integer32 | read-only | "0.1A" | current
[6 empty] | upsBypassCurrC | Bypass current C | .1.3.6.1.4.1.60967.1.2.3.4.6 | Integer32 | read-only | "0.1A" | current
[6 empty] | upsBypassFreqA | Bypass frequency A | .1.3.6.1.4.1.60967.1.2.3.4.7 | Integer32 | read-only | "0.1Hz" | current
[6 empty] | upsBypassFreqB | Bypass frequency B | .1.3.6.1.4.1.60967.1.2.3.4.8 | Integer32 | read-only | "0.1Hz" | current
[6 empty] | upsBypassFreqC | Bypass frequency C | .1.3.6.1.4.1.60967.1.2.3.4.9 | Integer32 | read-only | "0.1Hz" | current
[6 empty] | upsBypassPFA | Bypass power factor A | .1.3.6.1.4.1.60967.1.2.3.4.10 | Integer32 | read-only | "0.01" | current
[6 empty] | upsBypassPFB | Bypass power factor B | .1.3.6.1.4.1.60967.1.2.3.4.11 | Integer32 | read-only | "0.01" | current
[6 empty] | upsBypassPFC | Bypass power factor C | .1.3.6.1.4.1.60967.1.2.3.4.12 | Integer32 | read-only | "0.01" | current
[5 empty] | upsInput | upsInputVoltA | Input voltage A | .1.3.6.1.4.1.60967.1.2.3.5.1 | Integer32 | read-only | "0.1V" | current
[6 empty] | upsInputVoltB | Input voltage B | .1.3.6.1.4.1.60967.1.2.3.5.2 | Integer32 | read-only | "0.1V" | current
[6 empty] | upsInputVoltC | Input voltage C | .1.3.6.1.4.1.60967.1.2.3.5.3 | Integer32 | read-only | "0.1V" | current
[6 empty] | upsInputCurrA | Input current A | .1.3.6.1.4.1.60967.1.2.3.5.4 | Integer32 | read-only | "0.1A" | current
[6 empty] | upsInputCurrB | Input current B | .1.3.6.1.4.1.60967.1.2.3.5.5 | Integer32 | read-only | "0.1A" | current
[6 empty] | upsInputCurrC | Input current C | .1.3.6.1.4.1.60967.1.2.3.5.6 | Integer32 | read-only | "0.1A" | current
[6 empty] | upsInputFreqA | Input frequency A | .1.3.6.1.4.1.60967.1.2.3.5.7 | Integer32 | read-only | "0.1Hz" | current
[6 empty] | upsInputFreqB | Input frequency B | .1.3.6.1.4.1.60967.1.2.3.5.8 | Integer32 | read-only | "0.1Hz" | current
[6 empty] | upsInputFreqC | Input frequency C | .1.3.6.1.4.1.60967.1.2.3.5.9 | Integer32 | read-only | "0.1Hz" | current
[6 empty] | upsInputPFA | Input power factor A | .1.3.6.1.4.1.60967.1.2.3.5.10 | Integer32 | read-only | "0.01" | current
[6 empty] | upsInputPFB | Input power factor B | .1.3.6.1.4.1.60967.1.2.3.5.11 | Integer32 | read-only | "0.01" | current
[6 empty] | upsInputPFC | Input power factor C | .1.3.6.1.4.1.60967.1.2.3.5.12 | Integer32 | read-only | "0.01" | current
[6 empty] | upsInputLines | Input phase number | .1.3.6.1.4.1.60967.1.2.3.5.13 | Integer32 | read-only |  | current
[5 empty] | upsOutput | upsOutputVoltA | Output voltage A | .1.3.6.1.4.1.60967.1.2.3.6.1 | Integer32 | read-only | "0.1V" | current
[6 empty] | upsOutputVoltB | Output voltage B | .1.3.6.1.4.1.60967.1.2.3.6.2 | Integer32 | read-only | "0.1V" | current
[6 empty] | upsOutputVoltC | Output voltage C | .1.3.6.1.4.1.60967.1.2.3.6.3 | Integer32 | read-only | "0.1V" | current
[6 empty] | upsOutputCurrA | Output current A | .1.3.6.1.4.1.60967.1.2.3.6.4 | Integer32 | read-only | "0.1A" | current
[6 empty] | upsOutputCurrB | Output current B | .1.3.6.1.4.1.60967.1.2.3.6.5 | Integer32 | read-only | "0.1A" | current
[6 empty] | upsOutputCurrC | Output current C | .1.3.6.1.4.1.60967.1.2.3.6.6 | Integer32 | read-only | "0.1A" | current
[6 empty] | upsOutputFreqA | Output frequency A | .1.3.6.1.4.1.60967.1.2.3.6.7 | Integer32 | read-only | "0.01Hz" | current
[6 empty] | upsOutputFreqB | Output frequency B | .1.3.6.1.4.1.60967.1.2.3.6.8 | Integer32 | read-only | "0.01Hz" | current
[6 empty] | upsOutputFreqC | Output frequency C | .1.3.6.1.4.1.60967.1.2.3.6.9 | Integer32 | read-only | "0.01Hz" | current
[6 empty] | upsOutputPFA | Output power factor A | .1.3.6.1.4.1.60967.1.2.3.6.10 | Integer32 | read-only | "0.01" | current
[6 empty] | upsOutputPFB | Output power factor B | .1.3.6.1.4.1.60967.1.2.3.6.11 | Integer32 | read-only | "0.01" | current
[6 empty] | upsOutputPFC | Output power factor C | .1.3.6.1.4.1.60967.1.2.3.6.12 | Integer32 | read-only | "0.01" | current
[6 empty] | upsOutputKvaA | Output apparent power A | .1.3.6.1.4.1.60967.1.2.3.6.13 | Integer32 | read-only | "0.01kVA" | current
[6 empty] | upsOutputKvaB | Output apparent power B | .1.3.6.1.4.1.60967.1.2.3.6.14 | Integer32 | read-only | "0.01kVA" | current
[6 empty] | upsOutputKvaC | Output apparent power C | .1.3.6.1.4.1.60967.1.2.3.6.15 | Integer32 | read-only | "0.01kVA" | current
[6 empty] | upsOutputKwA | Output active power A | .1.3.6.1.4.1.60967.1.2.3.6.16 | Integer32 | read-only | "0.01kW" | current
[6 empty] | upsOutputKwB | Output active power B | .1.3.6.1.4.1.60967.1.2.3.6.17 | Integer32 | read-only | "0.01kW" | current
[6 empty] | upsOutputKwC | Output active power C | .1.3.6.1.4.1.60967.1.2.3.6.18 | Integer32 | read-only | "0.01kW" | current
[6 empty] | upsOutputKvarA | Output reactive power A | .1.3.6.1.4.1.60967.1.2.3.6.19 | Integer32 | read-only | "0.01kVar" | current
[6 empty] | upsOutputKvarB | Output reactive power B | .1.3.6.1.4.1.60967.1.2.3.6.20 | Integer32 | read-only | "0.01kVar" | current
[6 empty] | upsOutputKvarC | Output reactive power C | .1.3.6.1.4.1.60967.1.2.3.6.21 | Integer32 | read-only | "0.01kVar" | current
[6 empty] | upsOutputPercentA | Output load percentage A | .1.3.6.1.4.1.60967.1.2.3.6.22 | Integer32 | read-only | "0.1%" | current
[6 empty] | upsOutputPercentB | Output load percentage B | .1.3.6.1.4.1.60967.1.2.3.6.23 | Integer32 | read-only | "0.1%" | current
[6 empty] | upsOutputPercentC | Output load percentage C | .1.3.6.1.4.1.60967.1.2.3.6.24 | Integer32 | read-only | "0.1%" | current
[6 empty] | upsOutputLines | Output phase number | .1.3.6.1.4.1.60967.1.2.3.6.25 | Integer32 | read-only |  | current
[5 empty] | upsBattery | upsBatteryVoltPos | Battery voltage + | .1.3.6.1.4.1.60967.1.2.3.7.1 | Integer32 | read-only | "0.1V" | current
[6 empty] | upsBatteryVoltNeg | Battery voltage- | .1.3.6.1.4.1.60967.1.2.3.7.2 | Integer32 | read-only | "0.1V" | current
[6 empty] | upsBatteryCurrPos | Battery Current+ | .1.3.6.1.4.1.60967.1.2.3.7.3 | Integer32 | read-only | "0.1A" | current
[6 empty] | upsBatteryCurrNeg | Battery Current- | .1.3.6.1.4.1.60967.1.2.3.7.4 | Integer32 | read-only | "0.1A" | current
[6 empty] | upsBatteryCapacity | Battery capacity | .1.3.6.1.4.1.60967.1.2.3.7.5 | Integer32 | read-only | "0.1%" | current
[6 empty] | upsRemainTime | time left | .1.3.6.1.4.1.60967.1.2.3.7.6 | Integer32 | read-only | "minute" | current
[6 empty] | upsBatteryTemp | Battery temperature | .1.3.6.1.4.1.60967.1.2.3.7.7 | Integer32 | read-only | "0.1 Celsius" | current
[5 empty] | upsAlarms | upsCommunicationLost | Communication abnormality | .1.3.6.1.4.1.60967.1.2.3.8.1 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsIntegratedAlarm | Comprehensive alarm | .1.3.6.1.4.1.60967.1.2.3.8.2 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsEmergencyPowerOff | Emergency shutdown | .1.3.6.1.4.1.60967.1.2.3.8.3 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsBypassFault | Bypass failure | .1.3.6.1.4.1.60967.1.2.3.8.4 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsInputFault | Input failure | .1.3.6.1.4.1.60967.1.2.3.8.5 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsOutputFault | Output Fault | .1.3.6.1.4.1.60967.1.2.3.8.6 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsFanFault | Fan failure | .1.3.6.1.4.1.60967.1.2.3.8.7 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsBatteryFault | Battery failure | .1.3.6.1.4.1.60967.1.2.3.8.8 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsBatteryNotCnt | Battery No | .1.3.6.1.4.1.60967.1.2.3.8.9 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsBatteryVoltLow | Low battery voltage | .1.3.6.1.4.1.60967.1.2.3.8.10 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsRectifierFault | Rectifier failure | .1.3.6.1.4.1.60967.1.2.3.8.11 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsInverterFault | Inverter failure | .1.3.6.1.4.1.60967.1.2.3.8.12 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsOutputOverLoad | Output overload | .1.3.6.1.4.1.60967.1.2.3.8.13 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsOutputShortCircuit | Output short circuit | .1.3.6.1.4.1.60967.1.2.3.8.14 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsMaintOverTime | Maintenance time is up | .1.3.6.1.4.1.60967.1.2.3.8.15 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsBatteryDischarge | Battery discharge | .1.3.6.1.4.1.60967.1.2.3.8.16 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsSourceOnBypass | Bypass power supply | .1.3.6.1.4.1.60967.1.2.3.8.17 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsMaintSwitchOn | Maintenance circuit breaker closing | .1.3.6.1.4.1.60967.1.2.3.8.18 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsOverTemperature | UPS over temperature | .1.3.6.1.4.1.60967.1.2.3.8.19 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsBatteryTest | Battery maintenance | .1.3.6.1.4.1.60967.1.2.3.8.20 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsBatteryTestFail | Battery maintenance failed | .1.3.6.1.4.1.60967.1.2.3.8.21 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsBatteryTestOk | Battery maintenance successful | .1.3.6.1.4.1.60967.1.2.3.8.22 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsChargerFault | Battery or charger abnormality | .1.3.6.1.4.1.60967.1.2.3.8.23 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsOutputOffAsRequested | Manually shut off output | .1.3.6.1.4.1.60967.1.2.3.8.24 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsUpsOffAsRequested | Manual shutdown | .1.3.6.1.4.1.60967.1.2.3.8.25 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsUpsOutputOff | Output off | .1.3.6.1.4.1.60967.1.2.3.8.26 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsUpsSystemOff | Shut down the entire machine | .1.3.6.1.4.1.60967.1.2.3.8.27 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsFuseFault | Bypass power supply fuse failure | .1.3.6.1.4.1.60967.1.2.3.8.28 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsAwaitingPower | Output is turned off and waiting for mains power to be restored | .1.3.6.1.4.1.60967.1.2.3.8.29 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsShutdownPending | Countdown to shutdown | .1.3.6.1.4.1.60967.1.2.3.8.30 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | upsShutdownImminent | UPS is about to shut down the output | .1.3.6.1.4.1.60967.1.2.3.8.31 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
AC
|  |  |  | ac | acIndex | acDevTotalNums | Number of devices | .1.3.6.1.4.1.60967.1.2.4.1.1 | Integer32 | read-only |  | current | The number of ac in the system
[6 empty] | acCurrentDevID | Current device ID | .1.3.6.1.4.1.60967.1.2.4.1.2 | Integer32 | read-write |  | current | The current ac index of the follow data
[5 empty] | acIdentify | acManufacturer | Equipment Manufacturer | .1.3.6.1.4.1.60967.1.2.4.2.1 | OCTET STRING | read-write |  | current
[6 empty] | acSoftwareVersion | Software version | .1.3.6.1.4.1.60967.1.2.4.2.2 | OCTET STRING | read-only |  | current
[6 empty] | acDevIdentify | Device identification | .1.3.6.1.4.1.60967.1.2.4.2.3 | OCTET STRING | read-write |  | current
[5 empty] | acStatus | acSysRunStatus | System operating status | .1.3.6.1.4.1.60967.1.2.4.3.1 | INTEGER{none(0),localOff(146),powerOn(9),faultOff(301),standBy(302),stopping(303),remoteOff(147)} | read-only |  | current
[6 empty] | acCooling | Refrigeration status | .1.3.6.1.4.1.60967.1.2.4.3.2 | INTEGER{no(3),yes(4)} | read-only |  | current
[6 empty] | acHeating | Heating status | .1.3.6.1.4.1.60967.1.2.4.3.3 | INTEGER{no(3),yes(4)} | read-only |  | current
[6 empty] | acHumidifying | Humidification status | .1.3.6.1.4.1.60967.1.2.4.3.4 | INTEGER{no(3),yes(4)} | read-only |  | current
[6 empty] | acDehumidifying | Dehumidification state | .1.3.6.1.4.1.60967.1.2.4.3.5 | INTEGER{no(3),yes(4)} | read-only |  | current
[6 empty] | acBlowing | Air supply status | .1.3.6.1.4.1.60967.1.2.4.3.6 | INTEGER{no(3),yes(4)} | read-only |  | current
[6 empty] | acControlWays | Control method | .1.3.6.1.4.1.60967.1.2.4.3.7 | INTEGER{inletControl(70),outletControl(71)} | read-only |  | current
[5 empty] | acPara | acInletTemperature | Return air temperature | .1.3.6.1.4.1.60967.1.2.4.4.1 | Integer32 | read-only | "0.1 Celsius" | current
[6 empty] | acInletHumidity | Return air humidity | .1.3.6.1.4.1.60967.1.2.4.4.2 | Integer32 | read-only | "0.1%" | current
[6 empty] | acOutletTemperature | Supply air temperature | .1.3.6.1.4.1.60967.1.2.4.4.3 | Integer32 | read-only | "0.1 Celsius" | current
[6 empty] | acOutletHumidity | Supply air humidity | .1.3.6.1.4.1.60967.1.2.4.4.4 | Integer32 | read-only | "0.1%" | current
[5 empty] | acConfig | acOnOffControl | Power on/off control | .1.3.6.1.4.1.60967.1.2.4.5.1 | INTEGER{OFF(10),ON(9)} | read-write |  | current
[6 empty] | acTemperatureSetting | Temperature settings | .1.3.6.1.4.1.60967.1.2.4.5.2 | Integer32 | read-write | "0.1 Celsius" | current
[6 empty] | acHumiditySetting | Humidity setting | .1.3.6.1.4.1.60967.1.2.4.5.3 | Integer32 | read-write | "0.1%" | current
[6 empty] | acAlarmClear | Alarm reset | .1.3.6.1.4.1.60967.1.2.4.5.4 | INTEGER{no(0),clear(69)} | read-write |  | current
[5 empty] | acAlarms | acCommunicationLost | Communication abnormality | .1.3.6.1.4.1.60967.1.2.4.6.1 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acIntegratedAlarm | Comprehensive alarm | .1.3.6.1.4.1.60967.1.2.4.6.2 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acHighTemperature | High temperature alarm | .1.3.6.1.4.1.60967.1.2.4.6.3 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acLowTemperature | Low temperature alarm | .1.3.6.1.4.1.60967.1.2.4.6.4 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acHighHumidity | High humidity alarm | .1.3.6.1.4.1.60967.1.2.4.6.5 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acLowHumidity | Low humidity alarm | .1.3.6.1.4.1.60967.1.2.4.6.6 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acSmokeAlarm | Smoke alarm | .1.3.6.1.4.1.60967.1.2.4.6.7 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acLeakAlarm | Water leak alarm | .1.3.6.1.4.1.60967.1.2.4.6.8 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acDrainWaterFault | Drainage failure | .1.3.6.1.4.1.60967.1.2.4.6.9 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acPowerFault | Power failure | .1.3.6.1.4.1.60967.1.2.4.6.10 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acSensorFault | Sensor failure | .1.3.6.1.4.1.60967.1.2.4.6.11 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acFilterBlocking | Filter is clogged | .1.3.6.1.4.1.60967.1.2.4.6.12 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acMaintOverTime | Maintenance time is up | .1.3.6.1.4.1.60967.1.2.4.6.13 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acNetworkingAlarm | Network alarm | .1.3.6.1.4.1.60967.1.2.4.6.14 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acCompressorAlarm | Compressor alarm | .1.3.6.1.4.1.60967.1.2.4.6.15 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acVfdAlarm | Inverter alarm | .1.3.6.1.4.1.60967.1.2.4.6.16 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acHumidifierAlarm | Humidifier alarm | .1.3.6.1.4.1.60967.1.2.4.6.17 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acHeaterAlarm | Heater alarm | .1.3.6.1.4.1.60967.1.2.4.6.18 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acEvaporationFanAlarm | Internal fan alarm | .1.3.6.1.4.1.60967.1.2.4.6.19 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | acCondensateFanAlarm | External fan alarm | .1.3.6.1.4.1.60967.1.2.4.6.20 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
PDS
|  |  |  | pds | pdsIndex | pdsDevTotalNums | Number of devices | .1.3.6.1.4.1.60967.1.2.5.1.1 | Integer32 | read-only |  | current | The number of pds in the system
[6 empty] | pdsCurrentDevID | Current device ID | .1.3.6.1.4.1.60967.1.2.5.1.2 | Integer32 | read-write |  | current | The current pds index of the follow data
[5 empty] | pdsIdentify | pdsManufpdsturer | Equipment Manufacturer | .1.3.6.1.4.1.60967.1.2.5.2.1 | OCTET STRING | read-write |  | current
[6 empty] | pdsSoftwareVersion | Software version | .1.3.6.1.4.1.60967.1.2.5.2.2 | OCTET STRING | read-only |  | current
[6 empty] | pdsDevIdentify | Device identification | .1.3.6.1.4.1.60967.1.2.5.2.3 | OCTET STRING | read-write |  | current
[5 empty] | pdsMain | pdsMainTotalNums | Number of main roads | .1.3.6.1.4.1.60967.1.2.5.3.1 | Integer32 | read-only |  | current
[6 empty] | pdsMainCurrentID | Current main road ID | .1.3.6.1.4.1.60967.1.2.5.3.2 | Integer32 | read-write |  | current
[6 empty] | pdsMainOnOf | switch | .1.3.6.1.4.1.60967.1.2.5.3.3 | INTEGER{none(0),ON(1),OFF(2)} | read-only |  | current
[6 empty] | pdsMainLineVoltAB | AB line voltage | .1.3.6.1.4.1.60967.1.2.5.3.4 | Integer32 | read-only | "0.1V" | current
[6 empty] | pdsMainLineVoltBC | BC line voltage | .1.3.6.1.4.1.60967.1.2.5.3.5 | Integer32 | read-only | "0.1V" | current
[6 empty] | pdsMainLineVoltCA | CA line voltage | .1.3.6.1.4.1.60967.1.2.5.3.6 | Integer32 | read-only | "0.1V" | current
[6 empty] | pdsMainPhraseVoltA | Phase A voltage | .1.3.6.1.4.1.60967.1.2.5.3.7 | Integer32 | read-only | "0.1V" | current
[6 empty] | pdsMainPhraseVoltB | Phase B voltage | .1.3.6.1.4.1.60967.1.2.5.3.8 | Integer32 | read-only | "0.1V" | current
[6 empty] | pdsMainPhraseVoltC | Phase C voltage | .1.3.6.1.4.1.60967.1.2.5.3.9 | Integer32 | read-only | "0.1V" | current
[6 empty] | pdsMainPhraseVoltN | Neutral voltage | .1.3.6.1.4.1.60967.1.2.5.3.10 | Integer32 | read-only | "0.1V" | current
[6 empty] | pdsMainCurrentA | Phase A current | .1.3.6.1.4.1.60967.1.2.5.3.11 | Integer32 | read-only | "0.1A" | current
[6 empty] | pdsMainCurrentB | Phase B current | .1.3.6.1.4.1.60967.1.2.5.3.12 | Integer32 | read-only | "0.1A" | current
[6 empty] | pdsMainCurrentC | Phase C current | .1.3.6.1.4.1.60967.1.2.5.3.13 | Integer32 | read-only | "0.1A" | current
[6 empty] | pdsMainCurrentN | Zero-sequence current | .1.3.6.1.4.1.60967.1.2.5.3.14 | Integer32 | read-only | "0.1A" | current
[6 empty] | pdsMainFrequencyA | Phase A frequency | .1.3.6.1.4.1.60967.1.2.5.3.15 | Integer32 | read-only | "0.01Hz" | current
[6 empty] | pdsMainFrequencyB | Phase B frequency | .1.3.6.1.4.1.60967.1.2.5.3.16 | Integer32 | read-only | "0.01Hz" | current
[6 empty] | pdsMainFrequencyC | Phase C frequency | .1.3.6.1.4.1.60967.1.2.5.3.17 | Integer32 | read-only | "0.01Hz" | current
[6 empty] | pdsMainPfA | Phase A power factor | .1.3.6.1.4.1.60967.1.2.5.3.18 | Integer32 | read-only | "0.01" | current
[6 empty] | pdsMainPfB | Phase B power factor | .1.3.6.1.4.1.60967.1.2.5.3.19 | Integer32 | read-only | "0.01" | current
[6 empty] | pdsMainPfC | Phase C power factor | .1.3.6.1.4.1.60967.1.2.5.3.20 | Integer32 | read-only | "0.01" | current
[6 empty] | pdsMainPfAll | Total power factor | .1.3.6.1.4.1.60967.1.2.5.3.21 | Integer32 | read-only | "0.01" | current
[6 empty] | pdsMainLoadrateA | A phase load factor | .1.3.6.1.4.1.60967.1.2.5.3.22 | Integer32 | read-only | "0.1%" | current
[6 empty] | pdsMainLoadrateB | B phase load factor | .1.3.6.1.4.1.60967.1.2.5.3.23 | Integer32 | read-only | "0.1%" | current
[6 empty] | pdsMainLoadrateC | Phase C load factor | .1.3.6.1.4.1.60967.1.2.5.3.24 | Integer32 | read-only | "0.1%" | current
[6 empty] | pdsMainVoltUnbalance | Voltage imbalance rate | .1.3.6.1.4.1.60967.1.2.5.3.25 | Integer32 | read-only | "0.1%" | current
[6 empty] | pdsMainKvaA | Phase A apparent power | .1.3.6.1.4.1.60967.1.2.5.3.26 | Integer32 | read-only | "0.01kVA" | current
[6 empty] | pdsMainKvaB | B phase apparent power | .1.3.6.1.4.1.60967.1.2.5.3.27 | Integer32 | read-only | "0.01kVA" | current
[6 empty] | pdsMainKvaC | Phase C apparent power | .1.3.6.1.4.1.60967.1.2.5.3.28 | Integer32 | read-only | "0.01kVA" | current
[6 empty] | pdsMainKwA | Phase A active power | .1.3.6.1.4.1.60967.1.2.5.3.29 | Integer32 | read-only | "0.01kW" | current
[6 empty] | pdsMainKwB | Phase B active power | .1.3.6.1.4.1.60967.1.2.5.3.30 | Integer32 | read-only | "0.01kW" | current
[6 empty] | pdsMainKwC | Phase C active power | .1.3.6.1.4.1.60967.1.2.5.3.31 | Integer32 | read-only | "0.01kW" | current
[6 empty] | pdsMainKvarA | Phase A reactive power | .1.3.6.1.4.1.60967.1.2.5.3.32 | Integer32 | read-only | "0.01kVar" | current
[6 empty] | pdsMainKvarB | B phase reactive power | .1.3.6.1.4.1.60967.1.2.5.3.33 | Integer32 | read-only | "0.01kVar" | current
[6 empty] | pdsMainKvarC | Phase C reactive power | .1.3.6.1.4.1.60967.1.2.5.3.34 | Integer32 | read-only | "0.01kVar" | current
[6 empty] | pdsMainKwhA | Phase A active power | .1.3.6.1.4.1.60967.1.2.5.3.35 | Integer32 | read-only | "0.01kWH" | current
[6 empty] | pdsMainKwhB | Phase B active power | .1.3.6.1.4.1.60967.1.2.5.3.36 | Integer32 | read-only | "0.01kWH" | current
[6 empty] | pdsMainKwhC | Phase C active power | .1.3.6.1.4.1.60967.1.2.5.3.37 | Integer32 | read-only | "0.01kWH" | current
[6 empty] | pdsMainKwhAll | Total active power | .1.3.6.1.4.1.60967.1.2.5.3.38 | Integer32 | read-only | "0.01kWH" | current
[6 empty] | pdsMainKvarhA | Phase A reactive power | .1.3.6.1.4.1.60967.1.2.5.3.39 | Integer32 | read-only | "0.01kVarH" | current
[6 empty] | pdsMainKvarhB | B phase reactive power | .1.3.6.1.4.1.60967.1.2.5.3.40 | Integer32 | read-only | "0.01kVarH" | current
[6 empty] | pdsMainKvarhC | Phase C reactive power | .1.3.6.1.4.1.60967.1.2.5.3.41 | Integer32 | read-only | "0.01kVarH" | current
[6 empty] | pdsMainKvarhAll | Total reactive power | .1.3.6.1.4.1.60967.1.2.5.3.42 | Integer32 | read-only | "0.01kVarH" | current
[6 empty] | pdsMainVoltThdA | Phase A voltage THD | .1.3.6.1.4.1.60967.1.2.5.3.43 | Integer32 | read-only | "0.1%" | current
[6 empty] | pdsMainVoltThdB | Phase B voltage THD | .1.3.6.1.4.1.60967.1.2.5.3.44 | Integer32 | read-only | "0.1%" | current
[6 empty] | pdsMainVoltThdC | Phase C voltage THD | .1.3.6.1.4.1.60967.1.2.5.3.45 | Integer32 | read-only | "0.1%" | current
[6 empty] | pdsMainCurrentThdA | Phase A current THD | .1.3.6.1.4.1.60967.1.2.5.3.46 | Integer32 | read-only | "0.1%" | current
[6 empty] | pdsMainCurrentThdB | Phase B current THD | .1.3.6.1.4.1.60967.1.2.5.3.47 | Integer32 | read-only | "0.1%" | current
[6 empty] | pdsMainCurrentThdC | Phase C current THD | .1.3.6.1.4.1.60967.1.2.5.3.48 | Integer32 | read-only | "0.1%" | current
[5 empty] | pdsBranch | pdsBranchTotalNums | Number of branches | .1.3.6.1.4.1.60967.1.2.5.4.1 | Integer32 | read-only |  | current
[6 empty] | pdsBranchCurrentID | Current branch ID | .1.3.6.1.4.1.60967.1.2.5.4.2 | Integer32 | read-write |  | current
[6 empty] | pdsBranchOnOff | switch | .1.3.6.1.4.1.60967.1.2.5.4.3 | INTEGER{none(0),ON(1),OFF(2)} | read-only |  | current
[6 empty] | pdsBranchVolt | Voltage | .1.3.6.1.4.1.60967.1.2.5.4.4 | Integer32 | read-only | "0.1V" | current
[6 empty] | pdsBranchCurrent | Current | .1.3.6.1.4.1.60967.1.2.5.4.5 | Integer32 | read-only | "0.1A" | current
[6 empty] | pdsBranchLoadrate | Load factor | .1.3.6.1.4.1.60967.1.2.5.4.6 | Integer32 | read-only | "0.1%" | current
[6 empty] | pdsBranchPf | Power Factor | .1.3.6.1.4.1.60967.1.2.5.4.7 | Integer32 | read-only | "0.01" | current
[6 empty] | pdsBranchKva | Apparent power | .1.3.6.1.4.1.60967.1.2.5.4.8 | Integer32 | read-only | "0.01kVA" | current
[6 empty] | pdsBranchKw | Active power | .1.3.6.1.4.1.60967.1.2.5.4.9 | Integer32 | read-only | "0.01kW" | current
[6 empty] | pdsBranchKvar | Reactive power | .1.3.6.1.4.1.60967.1.2.5.4.10 | Integer32 | read-only | "0.01kVar" | current
[6 empty] | pdsBranchKwh | Active energy | .1.3.6.1.4.1.60967.1.2.5.4.11 | Integer32 | read-only | "0.01kWH" | current
[6 empty] | pdsBranchKvarh | Reactive energy | .1.3.6.1.4.1.60967.1.2.5.4.12 | Integer32 | read-only | "0.01kVarH" | current
[6 empty] | pdsBranchVoltThd | Voltage THD | .1.3.6.1.4.1.60967.1.2.5.4.13 | Integer32 | read-only | "0.1%" | current
[6 empty] | pdsBranchCurrentThd | Current THD | .1.3.6.1.4.1.60967.1.2.5.4.14 | Integer32 | read-only | "0.1%" | current
[5 empty] | pdsAlarms | pdsCommunicationLost | Communication abnormality | .1.3.6.1.4.1.60967.1.2.5.5.1 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | pdsIntegratedAlarm | Comprehensive alarm | .1.3.6.1.4.1.60967.1.2.5.5.2 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | pdsInputFault | Input Abnormality | .1.3.6.1.4.1.60967.1.2.5.5.3 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | pdsMainCurrentOver | Main road flow | .1.3.6.1.4.1.60967.1.2.5.5.4 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | pdsMainVoltOver | Main circuit overvoltage | .1.3.6.1.4.1.60967.1.2.5.5.5 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | pdsBranchCurrentOver | Branch overcurrent | .1.3.6.1.4.1.60967.1.2.5.5.6 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
THS
|  |  |  | ths | thsIndex | thsDevTotalNums | Number of devices | .1.3.6.1.4.1.60967.1.2.6.1.1 | Integer32 | read-only |  | current | The number of ths in the system
[6 empty] | thsCurrentDevID | Current device ID | .1.3.6.1.4.1.60967.1.2.6.1.2 | Integer32 | read-write |  | current | The current ths index of the follow data
[5 empty] | thsIdentify | thsManufthsturer | Equipment Manufacturer | .1.3.6.1.4.1.60967.1.2.6.2.1 | OCTET STRING | read-write |  | current
[6 empty] | thsSoftwareVersion | Software version | .1.3.6.1.4.1.60967.1.2.6.2.2 | OCTET STRING | read-only |  | current
[6 empty] | thsDevIdentify | Device identification | .1.3.6.1.4.1.60967.1.2.6.2.3 | OCTET STRING | read-write |  | current
[5 empty] | thsPara | thsTemperature | temperature | .1.3.6.1.4.1.60967.1.2.6.3.1 | Integer32 | read-only | "0.1 Celsius" | current
[6 empty] | thsHumidity | humidity | .1.3.6.1.4.1.60967.1.2.6.3.2 | Integer32 | read-only | "0.1%" | current
[5 empty] | thsAlarms | thsCommunicationLost | Communication abnormality | .1.3.6.1.4.1.60967.1.2.6.4.1 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | thsHighTemperature | High temperature alarm | .1.3.6.1.4.1.60967.1.2.6.4.2 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | thsLowTemperature | Low temperature alarm | .1.3.6.1.4.1.60967.1.2.6.4.3 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | thsHighHumidity | High humidity alarm | .1.3.6.1.4.1.60967.1.2.6.4.4 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | thsLowHumidity | Low humidity alarm | .1.3.6.1.4.1.60967.1.2.6.4.5 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
LEAK
|  |  |  | leak | leakIndex | leakDevTotalNums | Number of devices | .1.3.6.1.4.1.60967.1.2.7.1.1 | Integer32 | read-only |  | current | The number of leak in the system
[6 empty] | leakCurrentDevID | Current device ID | .1.3.6.1.4.1.60967.1.2.7.1.2 | Integer32 | read-write |  | current | The current leak index of the follow data
[5 empty] | leakIdentify | leakManufleakturer | Equipment Manufacturer | .1.3.6.1.4.1.60967.1.2.7.2.1 | OCTET STRING | read-write |  | current
[6 empty] | leakSoftwareVersion | Software version | .1.3.6.1.4.1.60967.1.2.7.2.2 | OCTET STRING | read-only |  | current
[6 empty] | leakDevIdentify | Device identification | .1.3.6.1.4.1.60967.1.2.7.2.3 | OCTET STRING | read-write |  | current
[5 empty] | leakPara | leakSite | Leakage location | .1.3.6.1.4.1.60967.1.2.7.3.1 | Integer32 | read-only | "0.1m" | current
[5 empty] | leakAlarms | leakCommunicationLost | Communication abnormality | .1.3.6.1.4.1.60967.1.2.7.4.1 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | leakLeakAlarm | Water leak alarm | .1.3.6.1.4.1.60967.1.2.7.4.2 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
BMS
|  |  |  | bms | bmsIndex | bmsDevTotalNums | Number of devices | .1.3.6.1.4.1.60967.1.2.8.1.1 | Integer32 | read-only |  | current | The number of bms in the system
[6 empty] | bmsCurrentDevID | Current device ID | .1.3.6.1.4.1.60967.1.2.8.1.2 | Integer32 | read-write |  | current | The current bms index of the follow data
[5 empty] | bmsIdentify | bmsManufbmsturer | Equipment Manufacturer | .1.3.6.1.4.1.60967.1.2.8.2.1 | OCTET STRING | read-write |  | current
[6 empty] | bmsSoftwareVersion | Software version | .1.3.6.1.4.1.60967.1.2.8.2.2 | OCTET STRING | read-only |  | current
[6 empty] | bmsDevIdentify | Device identification | .1.3.6.1.4.1.60967.1.2.8.2.3 | OCTET STRING | read-write |  | current
[5 empty] | bmsGroup | bmsGroupNums | Number of battery packs | .1.3.6.1.4.1.60967.1.2.8.3.1 | Integer32 | read-only |  | current
[6 empty] | bmsCurrentGroupID | Current battery pack ID | .1.3.6.1.4.1.60967.1.2.8.3.2 | Integer32 | read-write |  | current
[6 empty] | bmsGroupVolt | Group voltage | .1.3.6.1.4.1.60967.1.2.8.3.3 | Integer32 | read-only | "0.1V" | current
[6 empty] | bmsGroupCurrent | Group current | .1.3.6.1.4.1.60967.1.2.8.3.4 | Integer32 | read-only | "0.1A" | current
[6 empty] | bmsGroupSoc | Group SOC | .1.3.6.1.4.1.60967.1.2.8.3.5 | Integer32 | read-only | "0.1%" | current
[6 empty] | bmsGroupSoh | Group SOH | .1.3.6.1.4.1.60967.1.2.8.3.6 | Integer32 | read-only | "0.1%" | current
[6 empty] | bmsGroupMaxCellVolt | Maximum voltage of a single cell | .1.3.6.1.4.1.60967.1.2.8.3.7 | Integer32 | read-only | "1mV" | current
[6 empty] | bmsGroupMinCellVolt | Minimum voltage of single cell | .1.3.6.1.4.1.60967.1.2.8.3.8 | Integer32 | read-only | "1mV" | current
[6 empty] | bmsGroupMaxCellTemp | Maximum temperature of monomer | .1.3.6.1.4.1.60967.1.2.8.3.9 | Integer32 | read-only | "0.1 Celsius" | current
[6 empty] | bmsGroupMinCellTemp | Minimum monomer temperature | .1.3.6.1.4.1.60967.1.2.8.3.10 | Integer32 | read-only | "0.1 Celsius" | current
[6 empty] | bmsGroupMaxCellResistance | Maximum internal resistance of a single cell | .1.3.6.1.4.1.60967.1.2.8.3.11 | Integer32 | read-only | "0.001 mΩ" | current
[6 empty] | bmsGroupMinCellResistance | Minimum internal resistance of a single cell | .1.3.6.1.4.1.60967.1.2.8.3.12 | Integer32 | read-only | "0.001 mΩ" | current
[5 empty] | bmsCell | bmsCellNums | Number of battery cells | .1.3.6.1.4.1.60967.1.2.8.4.1 | Integer32 | read-only |  | current
[6 empty] | bmsCurrentCellID | Current monomer ID | .1.3.6.1.4.1.60967.1.2.8.4.2 | Integer32 | read-write |  | current
[6 empty] | bmsCellVolt | Single cell voltage | .1.3.6.1.4.1.60967.1.2.8.4.3 | Integer32 | read-only | "1mV" | current
[6 empty] | bmsCellTemperature | Monomer temperature | .1.3.6.1.4.1.60967.1.2.8.4.4 | Integer32 | read-only | "0.1 Celsius" | current
[6 empty] | bmsCellResistance | Monomer internal resistance | .1.3.6.1.4.1.60967.1.2.8.4.5 | Integer32 | read-only | "0.001 mΩ" | current
[5 empty] | bmsAlarms | bmsCommunicationLost | Communication abnormality | .1.3.6.1.4.1.60967.1.2.8.5.1 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | bmsIntegratedAlarm | Comprehensive alarm | .1.3.6.1.4.1.60967.1.2.8.5.2 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current
[6 empty] | bmsSysProtect | System Protection | .1.3.6.1.4.1.60967.1.2.8.5.3 | INTEGER{none(0),normal(1),alarm(2)} | read-only |  | current